**TABLE OF CONTENTS**

**Page**

I INTERESTING FACTS-------------------------------------------------------------------------------------- -------------------1

**II NEWS FLASH!!!** --------------------------------------------------------------------------------------------------------------2

III **PHYSICS OF ELECTRICAL HAZARDS------------------------------------------------------------------------------- ---- --2**

**IV SAFETY IN THE HAMSHACK------------------------------------------------------------------------------------------------2**

1. Electrical Hazards-------------------------------------------------------------------------------------------------2
2. **SHOCK-------------------------------------------------------------------------------------- ----------------------- 2**
3. Arcing------------------------------------ --------------------------------------------------------------------------3
4. Toxic vapors----------------------------------------------------------------------------------------------------3
5. Ventricular fibrillation ----------------------------------------------------------------------------------3
6. ELECTROCUTION, AND CARDIAC ARREST ------------------------------------------------------------------3
7. FALLING FROM LADDERS---------------------------------------------------------------------------------------4
8. PERSONAL IMPACT S---------------------------------------------------------------------------------------------4

B. Specific Hazards------------------------------------------------------------------------------------------------------ 4

C**.** SOURCE OF HAZARDS--------------------------------------------------------------------------------------------------4

1. Electrical shock-----------------------------------------------------------------------------------------------4

2. Arcs--------------------------------------------------------------------------------------------------------------5 3. Lightning, arcs, and over voltages-----------------------------------------------------------------------5

4. Melting wires ----------------------------------------------------------------------------------------- ------ 5 5. Arcs due to parting of contacts---------------------------------------------------------------------------5

6. RF Burns--------------------------------------------------------------------------------------------------------5

7. Burns------------------------------------------------------------------------------------------------------------5

8. High voltage lines--------------------------------------------------------------------------------------------5

9. Ladders---------------------------------------------------------------------------------------------------------5

1. Avoidance---------------------------------------------------------------------------------------------------------------5
2. Inspections----------------------------------------------------------------------------------------------------------5
3. Adequate protection---------------------------------------------------------------------------------------------6
4. Safe practices------------------------------------------------------------------------------------------------------6
5. Never work alone-------------------------------------------------------------------------------------------------6
6. Notifying family members when working on equipment-----------------------------------------------6
7. Read manuals and brochures----------------------------------------------------------------------------------6
8. Adequate maintenance------------------------------------------------------------------------------------------6
9. Identify and correct problems---------------------------------------------------------------------------------6
10. Perform a safety and hazards analyses----------------------------------------------------------------------6
11. HAM RADIO OPERATORS MUST HAVE A CULTURE OF SAFETY--------------------------------------6
12. Basic electrical safety principles and adhering to safe practices---------------------------6
13. Protection against equipment malfunction-----------------------------------------------------6
14. Solid connections--- -----------------------------------------------------------------------------------6
15. Shorts-----------------------------------------------------------------------------------------------------6
16. SHEILDING AND COVERING CIRCUITS-------------------------------------------------------------6
17. CORROISION AND OVERHEATING------------------------------------------------------------------7
18. INFRARED INSPECTION--------------------------------------------------------------------------------7
19. Adequate illumination---------------------------------------------------------------------------------7
20. Jewelry----------------------------------------------------------------------------------------------------7
21. Covered or blocked connectors--------------------------------------------------------------------7
22. Extension cords in low lying areas and carrying capacity of same-------------------------7
23. Lifting of tools------------------------------------------------------------------------------------------7
24. Double insulated tools--------------------------------------------------------------------------------7
25. 2 wire outlets-------------------------------------------------------------------------------------------7
26. Wet environments-------------------------------------------------------------------------------------7
27. Communicating with others------------------------------------------------------------------------7
28. Inspect Electrical system and breakers by a licensed professional------------------------7
29. FLAME RESISTANT CLOTHING----------------------------------------------------------------------7
30. SYNTHETIC MATERIALS-------------------------------------------------------------------------------7
31. INSULATED RUBBER MATTS------------------------------------------------------------------------7
32. TOOLS WITH INSULATED HANDLES----------------------------------------------------------------7
33. Damaged Tools------------------------------------------------------------------------------------------7
34. CIRCUIT BREAKERS AND GROUND-FAULT CIRCUIT INTERUPTERS**-----------------------------------7** A. Standard Breakers-------------------------------------------------------------------------------------------7
35. Failures---------------------------------------------------------------------------------------------------------7
36. Tests ------------------------------------------------------------------------------------------------------------7
37. Maintenance--------------------------------------------------------------------------------------------------7
38. Ground Fault Circuit Interrupters------------------------------------------------------------------------8
39. GFCI principles of operation-------------------------------------------------------------------------------8
40. GFCI wall units------------------------------------------------------------------------------------------------8
41. GFCI tests------------------------------------------------------------------------------------------------------8
42. GFCI reset------------------------------------------------------------------------------------------------------8
43. Insurance Claims---------------------------------------------------------------------------------------------8
44. Records---------------------------------------------------------------------------------------------------------8
45. COMMON SENSE SAFETY PROCEDURES AND METHODS----------------------------------------------9
46. Situational awareness--------------------------------------------------------------------------------------9
47. Alertness-------------------------------------------------------------------------------------------------------9
48. Safe procedures----------------------------------------------------------------------------------------------9
49. Ask Questions-------------------------------------------------------------------------------------------------9
50. Use proper equipment-------------------------------------------------------------------------------------9
51. Never Assume!-----------------------------------------------------------------------------------------------9
52. Status of Equipment----------------------------------------------------------------------------------------9
53. Tag out Breakers/Equipment-----------------------------------------------------------------------------9
54. Clean and organized station and work area-----------------------------------------------------------9
55. Double check yourself--------------------------------------------------------------------------------------9
56. De-energize/ disconnect equipment when not in use----------------------------------------------9
57. Disconnect antenna or ground it when not in use---------------------------------------------------9
58. Inspect equipment and connections prior to use----------------------------------------------------9
59. Use checklists-------------------------------------------------------------------------------------------------9
60. Liquids----------------------------------------------------------------------------------------------------------9
61. 3 Prong Plugs--------------------------------------------------------------------------------------------------9
62. Surge protectors---------------------------------------------------------------------------------------------9
63. Proper overcurrent protection---------------------------------------------------------------------------9
64. Grounding or disconnecting of antennas--------------------------------------------------------------9
65. WARNING SIGNS---------------------------------------------------------------------------------------------9
66. Locked hamshack--------------------------------------------------------------------------------------------9
67. Unplug lamps or appliances prior to repair-----------------------------------------------------------9
68. Test the wires before touching---------------------------------------------------------------------------9
69. Plumbing or gas pipes--------------------------------------------------------------------------------------9
70. Proper training in use of tools/equipment------------------------------------------------------------9
71. Use ground fault circuit interrupters (GFCIs) with tools-------------------------------------------9
72. Power tool extension cord length-----------------------------------------------------------------------9

AB. Tool use near live wires or water pipes----------------------------------------------------------------9 AC. Cutting or drilling into walls----------------------------------------------------------------------------10

AD. Tool malfunction------------------------------------------------------------------------------------------10 AE. Insulated grips--------------------------------------------------------------------------------------------10

AF. Protective gear--------------------------------------------------------------------------------------------10

AG. Manufacturers warnings and instructions----------------------------------------------------------10

AH. Standing in water-----------------------------------------------------------------------------------------10

AI. Repair of equipment--------------------------------------------------------------------------- ----------10 AJ. Qualified Repairman -------------------------------------------------------------------------------------10 AK. Damp locations--------------------------------------------------------------------------------------------10

AL. Flammable and Combustible Liquids----------------------------------------------------------------10

AM. Proximity to power lines--------------------------------------------------------------------------------10 AN. Sizing of extension cords------------------------------------------------------------------- ------------10

AO. Fuses---------------------------------------------------------------------------------------------------------10

AP. Overheated components-------------------------------------------------------------------------------10

AQ. Non-conductive ladders--------------------------------------------------------------------------------11

AR. Halogen lights----------------------------------------------------------------------------------------------11

AS. Ground Fault Circuit Interrupters (GFCIs) used in damp/wet locations---------------------11

AT. Portable in-line Ground Fault Circuit Interrupter (GFCI) usage-------------------------------11 AU. Exposed receptacle boxes-----------------------------------------------------------------------------11 AV . Knowledge of locations of breakers/panels for emergency use----------------------------11

AX. Proper labelling of circuit breakers, fuses, and panels------------------------------------------11

AY. Exposed wires---------------------------------------------------------------------------------------------11

AZ. Tool guards------------------------------------------------------------------------------------------------11

BA. Access to circuit breakers/fuses and panels-------------------------------------------------------11

BB. Tips for working with power tools--------------------------------------------------------------------11

BC. Knots in extension cords--------------------------------------------------------------------------------12

BD. Inspection of cords prior to use----------------------------------------------------------------------12

BE. Octopus Connections------------------------------------------------------------------------------------12

BF. Overloading outlets and rewiring of outlets/breakers for 20 amps--------------------------12

BG. Pull the plug; not the cord------------------------------------------------------------------------------12

BH. Breaking of Third Prong on plugs---------------------------------------------------------------------12

BI. Replacement of 2 prong receptacles-----------------------------------------------------------------12

BJ. Replacement of supply cords on old equipment--------------------------------------------------12

BK. Exposed metal parts (groundings)--------------------- ----------------------------------------------12

BL. Use of extension cords for permanent wiring---------------------------------------------------12

BM. Extension cords to be used only for temporary purposes-----------------------------------12

BN. Keep extension cords away from heat, water and oil-----------------------------------------12

BO. Driving of vehicles over cords versus proper protection--------------------------------------12

BP. Wiring in old houses-----------------------------------------------------------------------------------12

BQ. Extension cords across doorways and under carpets-----------------------------------------12

BR. Tamper resistant receptacles for small children-------------------------------------------------13

BS. Replace temporary cords with permanent wiring and receptacles-------------------------13

BT. Avoid overloading outlets----------------------------------------------------------------------------13

BU. Overheated outlets, switches, etc.-----------------------------------------------------------------13

BV. Placement of Lamps------------------------------------------------------------------------------------13

BW. GFCI’s-----------------------------------------------------------------------------------------------------13

BY. Arc-fault Interrupters (AFCI’s)----------------------------------------------------------------------13

BZ. Smoke Alarms-------------------------------------------------------------------------------------------13

CA. Proper sizing of Lightbulbs--------------------------------------------------------------------------13

CB. Intermittent Circuits and components-----------------------------------------------------------13

1. Exposed wires, circuits, components, etc.------------------------------------------------------13

CD. Proper grounding necessary for proper function of overload safety devices-----------14

CE. Surge protectors----------------------------------------------------------------------------------------14

CF. Hire professionals to test, inspect and repair equipment-----------------------------------14

CG. Use of electrical equipment in wet and damp locations--------------------------------------14

VIII. GENERAL REQUIREMENTS FOR GROUNDING----------------------------------------------------------------------14

1. Electrical driven tools------------------------------------------------------------------------------------------14
2. Proper bonding and grounding of electrical equipment---------------------------------------------14
3. Noncurrent carrying metal parts----------------------------------------------------------------------------14
4. Exposed metal components and equipment-------------------------------------------------------------14
5. Grounds must be permanent and continuous-----------------------------------------------------------14
6. Must carry the maximum ground fault current---------------------------------------------------------14
7. Solder or sheet metal screws not permitted------------------------------------------------------------14
8. Protection from physical damage---------------------------------------------------------------------------14
9. Paint and coatings not permitted---------------------------------------------------------------------------14
10. Installation of ground rods/electrodes--------------------------------------------------------------------14
11. Must use best soil possible-----------------------------------------------------------------------------------15
12. Solid copper – best material---------------------------------------------------------------------------------15
13. Direct path to ground required---------------------------------------------------------------------------15
14. Ensure that good ground is provided--------------------------------------------------------------------15
15. Explore/identify locations of electrical system ground----------------------------------------------15
16. GROUND THE METAL CLAD, metal sheathed or grounded metal raceway wiring------------15
17. Metal Racks------------------------------------------------------------------------------------------------------15
18. No splices or joints allowed----------------------------------------------------------------------------------15
19. National Electric Code Requirements (NFPA 70) for grounding-------------------------------------15
20. NEC 250.66 size of conductor--------------------------------------------------------------------------15
21. Connections to Concrete-Encased Electrodes-----------------------------------------------------15
22. Ground Rings-----------------------------------------------------------------------------------------------15
23. Individual equipment-------------------------------------------------------------------------------------15
24. Table 250.122 of NEC- minimum sizes of Equipment Grounding Conductors based on the rating or setting of the automatic overcurrent device in the circuit ahead of the equipment---------------------------------- ----------------------------------------------------------------15
25. For a 15 amp circuit- minimum size of conductor-------------------------------------------------16
26. For a 20 amp circuit- minimum size of the ground conductor---------------------------------16
27. For a 60 amp circuit- minimum size of the ground conductor---------------------------------16
28. For a 100 amp circuit-the minimum size of the ground conductor---------------------------16
29. The minimum size of the main ground conductor that is connected to the ground electrode----------------------------------------------------------------------------------------------------16
30. The size of the conductor - largest service-entrance conductor or equivalent area of parallel conductors----------------------------------------------------------------------------------------16
31. NEC 250.68 (B) connection of grounding electrode conductor--------------------------------16
32. NEC 250.70 methods of connections-----------------------------------------------------------------16
33. Use of solder not allowed-------------------------------------------------------------------------------16
34. Grounding connections/joints must not to increase the resistance of the grounding system--------------------------------------------------------------------------------------------------------16
35. Proper mechanical methods and corrosion---------------------------------------------------------16
36. Note: IEEE Std 80, “Guide for Safety in Substation Grounding used as a guide----------16
37. Connectors and splice connections-------------------------------------------------------------------16
38. Always assume that components are energized at highest voltage and current available------------------------------------------------------------------------------------------------------------------17
39. NEC Section 250.114- proper grounding of cord and plug-connected equipment--------17
40. 3 prong plugs are now the standard for effective grounding-----------------------------------17
41. 2 prong adapters for 3 prong cabled equipment are no longer allowed--------------------17
42. NEC 250.118-types of equipment grounding conductors---------------------------------------17

IX BONDING----------------------------------------------------------------------------------------------------------------------17

1. Non-current-carrying electrical parts capable of conducting electricity---------------------------17
2. FUSES----------------------------------------------------------------------------------------------------------------- 17
3. Required inspections------------------------------------------------------------------------------------------17
4. Proper sizing--------------------------------------------------------------------------------- -------------------17
5. Non-high starting inrush current equipment -----------------------------------------------------------17
6. fuses located in both the negative and positive electrical power cords--------------------------17
7. Fuse mounting clips and hardware------------------------------------------------------------------------17
8. Dangerous shortcut-use of aluminum foil----------------------------------------------------------------18
9. BATTERIES-------------------------------------------------------------------------------------------------------18
10. Electrical hazards---------------------------------------------------------------------------------------------18

B. Chemical Hazards---------------------------------------------------------------------------------------------18

C. Explosion Hazards--------------------------------------------------------------------------------------------18

D. Safety Precautions-------------------------------------------------------------------------------------------18

E. . NATIONAL ELECTRIC CODE REQUIREMENTS FOR BATTERIES (NEC ARTICLE 480)------------ 19

1. NEC ARTICLE 480

a. 480.3 (A) Dissimilar Metals----------------------------------------------------------------------------------------19

b. 480.3 (B) Connections and conductors----------------------------------------------------------------------19

c. Adequate ventilation (NFPA Fire Code Chapter 52)-------------------------------------------------------19

d. NEC 480.8: (A) Racks and Trays---------------------------------------------------------------------------------20

e. Egress----------------------------------------------------------------------------------------------------------------20

f. Batteries prohibited where gas piping is present--------------------------------------------------------20

g. Lighting-------------------------------------------------------------------------------------------------------------20

h. Flame arrestors---------------------------------------------------------------------------------------------------20

i. Sealed cells--------------------------------------------------------------------------------------------------------20

1. INFORMATION TECHNOLGY EQUIPMENT/COMPUTERS (INCLUDES HAM RADIOS)-------------21
2. NATIONAL ELECTRIC CODE REQUIREMENTS - NEC 645-----------------------------------------21
3. NEC 645.5 Supply Circuits and Interconnecting Cables-------------------------------------21
4. Branch Circuit Connectors-------------------------------------------------------------------------21
5. The Branch Circuit Conductors ampacity-------------------------------------------------21
6. Power Supply Cords maximum length----------------------------------------------------21
7. Power Supply Cords-laboratory tested and labeled------------------------------------21
8. Cords- protected from physical damage---------------------------------------------------21
9. unused cables- laying around----------------------------------------------------------------21
10. NEC 645.15 Equipment Grounding and Bonding----------------------------------------------21
11. Doors-direction of egress---------------------------------------------------------------------------21
12. SOLAR POWER SYSTEMS- NEC 690--------------------------------------------------------------------------21
13. NEC 690.4: All equipment must be listed by UL or equivalent----------------------------------21
14. NEC 690.5 Ground Fault Protection-------------------------------------------------------------------21
15. Ground-Fault Detection System and Interruption---------------------------------------21
16. ground faults in the PV array, dc current carrying conductors and components including intentionally grounded conductors-------------------------------------------------------21
17. Must interrupt the flow of fault current---------------------------------------------------21
18. Must be listed for providing ground fault protection----------------------------------21
19. Overcurrent protection - NEC 240.5(b)(2)----------------------------------------------------------21
20. Conductors must comply with Article 240-----------------------------------------------------21
21. DC Arc Fault protection - NEC 690.11---------------------------------------------------------21
22. Rapid Shutdown method - NEC 690.12---------------------------------------------------------21
23. Disconnecting means - NEC 690.13 and NEC 690.17-----------------------------------------21
24. Must not be able to disconnect the ground conductor (NEC 690.17)-------------------21
25. Interruption of maximum voltage and current (NEC 690.17 (E))-------------------------21
26. Separation from the normal electrical system and its components (NEC 690.31)---21
27. Labeling of components--------------------------------------------------------------------------- 21
28. Solar Power System grounding - NEC 690.42-------------------------------------------------21

XIV GENERATORS**----------------------------------------------------------------------------------------------------------21**

1. Must comply with NEC Article 445-------------------------------------------------------------------------------21
2. NEC 445.12 Generator overload protection-------------------------------------------------------------21
3. Cables led from Generator - overcurrent protection --------------------------------------------------21
4. Conductors that must carry ground fault current in accordance with NEC 445.16-------------21
5. Requirements for cables passing through barriers-----------------------------------------------------21
6. NEC 445.20 Ground fault circuit Interrupter (GFCI) protection--------------------------------------22

XV. COMMUNICATIONS SYSTEMS----------------------------------------------------------------------------------22

A. Chapter 8 of the National Electric Code -------------------------------------------------------------------------22

1. Tagging of Abandoned cables----------------------------------------------------------------------------------22

2. NEC 800.24 Installation of Communications circuits, cables and equipment----------------------22

3. Cables installed on ceilings and walls------------------------------------------------------------------------22

4. Non-metallic hardware------------------------------------------------------------------------------------------22

5. Sealing of holes where cables run through walls, etc ---------------------------------------------------22

6. NEC 800.25 Accessible portions of abandoned cables--------------------------------------------------22

7. NEC 800.44 (A) Cables On Poles and In-Span--------------------------------------------------------------22

1. NEC 800.49 Metallic Conduit--------------------------------------------------------------------------------22
2. NEC 800.50 (C) Requirements for building entrances of communications cables and wires -------------------------------------------------------------------------------------------------------------------------22

10. NEC 800.53 Lightning Conductors for Communications systems---------------------------------23 11. NEC 800.90 A (Lightning Arrestor) Required in aerial wire--------------------------------------------23

1. Size of Ground rod wires---------------------------------------------------------------------------------23
2. Both communications and power grounding electrode systems must be connected together in single and 2 family dwelling-------------------------------------------------------------------23
3. Length and run of Grounding wires------------------------------------------------------------------------23
4. Grounding wires must be protected where exposed to physical damage------------------------23
5. Where separate grounding rods or means are provided for both communications cables/wires and power systems, they must be interconnected------------------------------------23
6. NEC 800.110 (C) (1) Communications cables/wires run horizontally ------------------------------23
7. NECn800.110 (C) (2) Vertical supports of communications cables/wires-------------------------23

XVI. RECEIVING ANTENNAS NEC 800--------------------------------------------------------------------------------------24

1. NEC 810.11 Material(s)------------------------------------------------------------------------------------------24
2. lead-in conductors where maximum span between supports is less than 35 feet----------24
3. NEC 810.12 Supports for wire strung Antennas-----------------------------------------------------------24

C. NEC 810.13 Avoidance of Contacts with Conductors of Other Systems-----------------------------24

1. When Proximity of lighting and power conductors below 250 volts cannot be avoided--24
2. Must not cross under open electric light or power conductors---------------------------------24
3. NEC 810.14 Splices in Receiving Antennas-----------------------------------------------------------------24
4. NEC 810.15 Groundings-----------------------------------------------------------------------------------------25
5. NEC 810.21 Masts and metal structures supporting antennas ---------------------------------25
6. NEC 810.16 size of wire strung receiving antennas------------------------------------------------------25
7. Must be sized not less than given in Table 810.16(A)-------------------------------------------25
8. Self-supporting Antennas---------------------------------------------------------------------------------------25
9. Outdoor antennas such as rods and flat, parabolic ,or dipole structures: corrosion resistant and strong enough to remain intact when coated with ice and withstand wind loading conditions-------------------------------------------------------------------------------------------25
10. Must be located to avoid the possibility of the antenna or structure falling into or making accidental contact with power electrical lines--------------------------------------------------------25
11. Lead-ins for Antennas
12. NEC 810.17 Size of Lead-in for Receiving Station antennas---------------------------------------25
13. Combined tensile strength of lead-ins containing more than one conductor----------------25
14. Lead-in conductors attached to house/building that are flexible--------------------------------25
15. lead-in conductors that are supported so as to ensure permanent separation--------------25
16. Clearance between antenna lead-in conductors and any conductor forming part of a lightning protection system ------------------------------------------------------------------------------25
17. Separation of Underground lead-in conductors from light or power circuits----------------25
18. Separation of Antennas and Lead-ins-Indoors from conductors of other wiring systems in the premises--------------------------------------------------------------------------------------------------25
19. In boxes and enclosures, Indoor antennas and indoor lead-ins may occupy the same box or enclosure with conductors of other wiring systems provided they are separated by an effective permanently installed barrier----------------------------------------------------------------26

XVII LIGHTNING PROTECTION SYSTEMS-----------------------------------------------------------------------------------26

1. NFPA 780-2014, Standard for the installation of Lightning Protection Systems-----------------------26
2. NFPA 780-2011, Standard for Installation of Lightning Protection Systems including requirements for antenna lead-in systems that are contained in metal raceways, enclosures, frames, and other non-current carrying metal parts of electrical equipment installed on buildings equipped with a lightning protection system-----------------------------------------------------------------26
3. bonding or spacing from lightning protection conductors------------------------------------------26
4. Separation requirements forf antenna lead-in conductors from lightning protection conductors -------------------------------------------------------------------------------------------------------26

2.. Materials of Bonding conductors and grounding electrode conductor s------------------------------26

1. Prohibition of Aluminum or copper-clad aluminum bonding conductors or grounding electrode conductors------------------------------------------------------------------------------------------26
2. Separation from earth where outside aluminum or copper-clad aluminum conductors are used.----------------------------------------------------------------------------------------------------------------26
3. Insulation is not required on bonding conductors or grounding electrode conductors------26
4. Fastening and attachment of Bonding conductors or grounding electrode conductor -------26
5. Sizing of Conductors where supports are not provided------------------------------------------------26
6. Protection of protectors where exposed to physical damage----------------------------------------27
7. Where bonding conductors and grounding electrode conductors are installed in a metal raceway, both ends of the raceway shall be bonded to the conductor-------------------------------27
8. Straight runs of Bonding conductors and grounding electrode conductors for antenna mast--27
9. Minimum Sizing of Bonding and ground electrode conductors ----------------------------------------27

XVII. TRANSMITTING ANTENNAS INCLUDING HAM RADIO ANTENNAS-------------------------------------------27

1. NEC 810.52 Size of Transmitting Antenna Conductors for ham radio stations--------------------27
2. Antennas where the open span length is less than 150 feet ------------------------------------------27
3. Antennas with open span length over 150 feet the minimum size of conductors-----------------27
4. NEC 810.54 Open Antenna conductors attached to buildings-----------------------------------------27
5. Supports--------------------------------------------------------------------------------------------------------------27
6. Metal sheathed coax cables and grounding in accordance with NEC 810.56-----------------------27
7. NEC 810.55 Lead-in conductors entering buildings--------------------------------------------------------27
8. rigid, non-combustible, nonabsorbent insulated tube or bushing-----------------------------27
9. openings provided for the purpose in which the entrance conductors are firmly supported---------------------------------------------------------------------------------------------------------------27
10. Through a drilled window pane------------------------------------------------------------------------27
11. NEC 810.56 Protection against Accidental Contact-------------------------------------------------------28
12. Lead in conductors to radio transmitters- installed and located as to make accidental contact with them difficult---------------------------------------------------------------------------------28
13. NEC810.57 Lightning Arrestors--------------------------------------------------------------------------------28
14. Unless grounded coax is used, antenna discharge units are required for transmitting stations. This is required for individual conductors.-------------------------------------------------28
15. NEC 810.58 (B) Size of Protective Bonding Conductor or Grounding Electrode Conductor for transmitting stations----------------------------------------------------------------------------------------------28
16. NEC 810.70 Separation Clearance of Antenna conductors and lead-ins from any electrical conductor for lighting, power or signaling circuit----------------------------------------------------------28

XIX HAM RADIO TRANSMITTERS-------------------------------------------------------------------------------------------28

1. NEC 810.71 Transmitters----------------------------------------------------------------------------------------28
2. Enclosures------------------------------------------------------------------------------------------------------ 28
3. Metal handles and controls accessible to the operating personnel must be in accordance with NEC 810.21--------------------------------------------------------------------------------------------- 28
4. Interlocks on Doors: All access doors shall be provided with interlocks that disconnect all voltages over 350 volts between conductors when the access door is opened--------28

XX FIRES----------------------------------------------------------------------------------------------------------------------------29

1. HAVE A PLAN-----------------------------------------------------------------------------------------------------------29
2. Children hide------------------------------------------------------------------------------------------------------------29
3. Alternate plan if the first one cannot be used due to location of fire.-----------------------------------29
4. If you are on a 2nd or higher floor----------------------------------------------------------------------------------29
5. Chained emergency ladder and hammer------------------------------------------------------------------- 29
6. Closed doors-----------------------------------------------------------------------------------------------------------29
7. Understand the science and chemistry of fires-----------------------------------------------------------------29
8. The fire triad: In order to have a fire, you have to have heat, fuel and oxygen. Take one of these away and the fire cannot exist-----------------------------------------------------------------------29
9. Different fuels/different fires/different types of fire extinguishing agents----------------------29
10. Types of Fires----------------------------------------------------------------------------------------------------29
11. Class A -------------------------------------------------------------------------------------------------------29
12. Class B --------------------------------------------------------------------------------------------------------29
13. **Class C fires-Electrical and Electronics equipment------------------------------------------------29**
14. Class D fires--------------------------------------------------------------------------------------------------29
15. Class K fires--------------------------------------------------------------------------------------------------29
16. Types of Fire Extinguishers and their applications:-----------------------------------------------------30
17. Water and Foam

**Water extinguishers are for Class A fires only ---------------------------------------------------30**

1. Carbon Dioxide extinguishers for Class B & C Fires-----------------------------------------------30
2. Dry Chemical extinguishers------------------------------------------------------------------------------30
3. Class C Electrical--------------------------------------------------------------------------------------------30
4. Multipurpose Dry Chemical------------------------------------------------------------------------------30
5. Wet Chemical extinguishers ----------------------------------------------------------------------------30
6. Clean Agent extinguishers -------------------------------------------------------------------------------31

1. Dry Powder extinguishers--------------------------------------------------------------------------------31

1. Water Mist extinguishers ---------------------------- --------------------------------------------------31

1. Cartridge-Operated Dry Chemical extinguishers -----------------------------------------------31
2. **How to size a fire-extinguisher-------------------------------------------------------------------------------------32**
3. Consider how quickly a fire could spread in the area and how long it might take you to become aware of the emergency---------------------------------------------------------------------------32
4. **Look at the size of the area and where fires are most likely to start. For a large room, consider a large extinguisher, such as a 10-pound model. For a small room, a 5-pound model should be sufficient.---------------------------------------------------------------------------------32**
5. lift and maneuverability-------------------------------------------------------------------------------------32
6. **How to use a fire extinguisher----------------------------------------------------------------------------------33**
7. Stand roughly 8 feet from the fire and hold the extinguisher in one hand----------------------33
8. Pull the pin on the fire extinguisher to release the handle. Toss the pin aside-----------------33
9. Aim the hose of the extinguisher at the base of the fire, not at the smoke or flames, then squeeze the handle firmly------------------------------------------------------------------------------------33
10. Sweep the contents of the extinguisher back and forth across the **base of the fire**, maintaining even pressure on the handle----------------------------------------------------------------33
11. Stop spraying the extinguisher once the fire has gone out and call 911 for help if needed. 33